## Sheet1
| ASHP - Sound Power Level |  | HEAT PUMP MODEL
STEP | INSTRUCTONS | RESULTS | RIELLO NXHM 006 - 6KW | [18 empty] | A | C | H
1 | From manufacturers data, obtain the A-weighted sound power level of the heat pump. See “Note 1: Sound Power Level” below. The highest sound power level specified should be used (the power in “low noise mode” should not be used). | 58 | LENGTH (MM) (A) | 1295 |  | HEATPUMP | [13 empty] | RIELLO NXHM 004 - 4KW | RIELLO 4KW | 1295 | 429 | 792
[6 empty] | SELECT | [13 empty] | RIELLO NXHM 006 - 6KW | RIELLO 6KW | 1295 | 429 | 792
2 | Use “Note 2: Sound Pressure level” and “Note 3: Determina on of direc vity” below to establish the direc vity “Q” of the heat pump noise. | Q4 - "Two Reflective Surfaces" | HEIGHT (MM) (H) | 792 |  | RIELLO NXHM 004 - 4KW | 55 | [12 empty] | RIELLO NXHM 008 - 8KW | RIELLO 8KW | 1295 | 526 | 945
[6 empty] | RIELLO NXHM 006 - 6KW | 58 | [12 empty] | RIELLO NXHM 010 - 10KW | RIELLO 10KW | 1295 | 526 | 945
3 | Measure the distance from the heat pump to the assessment posi on in metres. | 4 | DEPTH (MM) (C) | 429 |  | RIELLO NXHM 008 - 8KW | 59 | [12 empty] | RIELLO NXHM 012 - 12KW | RIELLO 12KW | 1295 | 526 | 945
[6 empty] | RIELLO NXHM 010 - 10KW | 60 | [12 empty] | RIELLO NXHM 014 - 14KW | RIELLO 14KW | 1295 | 526 | 945
4 | Use table in “Note 4: dB distance reduc on” below to obtain a dB reduc on. | -17 |  |  |  | RIELLO NXHM 012 - 12KW | 65 | [12 empty] | RIELLO NXHM 016 - 16KW | RIELLO 16KW | 1295 | 526 | 945
|  |  | HEATPUMP DIMENSIONS |  |  | RIELLO NXHM 014 - 14KW | 65
5 | Establish whether there is a solid barrier between the heat pump and the assessment posi on using “Note 5: Barriers between the heat pump and the assessment posi on” and note any dB reduc on. | Barrier (partial view) | #VALUE! |  |  | RIELLO NXHM 016 - 16KW | 68
6 | Calculate the sound pressure level (see Note 2: Sound pressure level”) from the heat pump at the assessment posi on using the following calcula on: (STEP 1) + (STEP 4) + (STEP 5) | 36
7 | Background noise level. For the purposes of the MCS Planning Standard for air source heat pumps the background noise level is assumed to be 40 dB (A)Lp. For informa on see “Note 6: MCS Planning Standard for air source heat pumps background noise level” | 40
8 | Determine the difference between STEP 7 background noise level and the heat pump noise level using the following calcula on: (STEP 7) – (STEP 6) | 4
9 | Using the table in “Note 7: Decibel correc on” obtain an adjustment figure and then add this to whichever is higher dB figure from STEP 6 and STEP 7. Round this number up to the nearest whole number. | 41.5 |  |  |  | RIELLO NXHM 004 - 4KW
RIELLO NXHM 004 - 4KW
9 | Using the table in “Note 7: Decibel correc on” obtain an adjustment figure and then add this to whichever is higher dB figure from STEP 6 and STEP 7. Round this number up to the nearest whole number. | 42
10 | Is the FINAL RESULT in STEP 9 lower than the permi ed development noise limit of 42 dB (A)? If YES – the air source heat pump will comply with the permi ed development noise limit for this assessment posi on and may be permi ed development (subject to compliance with other permi ed development limita ons/condi ons and parts of the MCS 020 standard.) MCS Contractors Results 9 41 YES NOTE – other assessment posi ons may also need to be tested. If NO – the air source heat pump will not be permi ed development. This installa on may s ll go ahead if planning permission is granted by the local planning authority. | Pass
Sound Pressure Level
Q2 - "One Reflective Surface"
Q4 - "Two Reflective Surfaces"
Q8 - "Three Reflective Surfaces"
dB distance reduction
Distance from Heat Pump (meters)
[6 empty] | 1 | 1.5 | 2 | 3 | 4 | 5 | 6 | 8 | 10 | 12 | 15 | 20 | 25 | 30
[5 empty] | Q2 | -8 | -11 | -14 | -17 | -20 | -21 | -23 | -26 | -28 | -29 | -31 | 34 | -36 | -37
[5 empty] | Q4 | -5 | -8 | -11 | -14 | -17 | -19 | -20 | -23 | -25 | -26 | -28 | -31 | -33 | -34
[5 empty] | Q8 | -2 | -5 | -8 | -11 | -14 | -16 | -17 | -20 | -22 | -23 | -25 | -28 | -30 | -31
[5 empty] | Barrier (no view) |  | -10
[5 empty] | Barrier (partial view) |  | -5
[5 empty] | Visible |  | 0
[5 empty] | Difference between the two noise levels |  |  | Add this correction to the higher noise level
[7 empty] | -15 | 0.1
[7 empty] | -14 | 0.2
[7 empty] | -13 | 0.2
[7 empty] | -12 | 0.3
[7 empty] | -11 | 0.3
[7 empty] | -10 | 0.4
[7 empty] | -9 | 0.5
[7 empty] | -8 | 0.6
[7 empty] | -7 | 0.8
[7 empty] | -6 | 1
[7 empty] | -5 | 1.2
[7 empty] | -4 | 1.5
[7 empty] | -3 | 1.8
[7 empty] | -2 | 2.1
[7 empty] | -1 | 2.5
[7 empty] | 0 | 3
[7 empty] | 1 | 2.5
[7 empty] | 2 | 2.1
[7 empty] | 3 | 1.8
[7 empty] | 4 | 1.5
[7 empty] | 5 | 1.2
[7 empty] | 6 | 1
[7 empty] | 7 | 0.8
[7 empty] | 8 | 0.6
[7 empty] | 9 | 0.5
[7 empty] | 10 | 0.4
[7 empty] | 11 | 0.3
[7 empty] | 12 | 0.3
[7 empty] | 13 | 0.2
[7 empty] | 14 | 0.2
[7 empty] | 15 | 0.1