| Jenni Perkins jenni.perkins@wrexham.gov.uk |  |  |
| --- | --- | --- |
|  | Eich Cyf/Your Ref: Ein Cyf/Our Ref: Dyddiad/Date: Gofynner am/Ask for: Rhif Union/Direct Dial: | P/2023/0500 80/ 000848- Slgen8a.Temp.2 29/11/2023 Jim Hughes 01286 662999 |

Dear Madam,

THE TOWN AND COUNTRY PLANNING ACT 1990 – CONSULTATION

PREMISES: 	Erection of storage & distribution warehouses – H Pack Packaging UK, Davy Way Industrial Estate, Llay

With reference to your consultation dated 23rd November 2023 and received on 24th November 2023, attached is our inspection report in respect of application P/2023/0500 with amended plans.

Providing that the requirements for access for fire appliances and water supplies are met so far as reasonably practicable, the Fire Authority will have no objections to this planning application.

If you should require any further information, please do not hesitate to contact the Compliance Officer.

Yn gywir/ Yours faithfully,

James Francis Hughes GIFireE

Authorised Fire Safety Inspecting Office

And on behalf of the North Wales Fire and Rescue Authority

ACCESS FOR FIRE APPLIANCE

Site access roads should ideally have minimum width of 3.7 metres

Minimum width between gateways of 3.1 metres (If applicable)

Road carrying capacity: Minimum of 12.5 Tonnes

TURNING FACILITIES:

Fire and Rescue Service appliances should not have to reverse more than 20 metres from the end of an access road.  This could be achieved by having turning circles, a hammerhead facility or other point at which the appliance can turn.

For further guidance refer to:

- Approved Document B – Fire safety, Volume 2 – Buildings other than dwelling houses, Section 17: Vehicle access B5 pages 166 to 171

- “Guide to Risk Assessment in Factories and warehouses” ISBN-13: 978 1 85112 816 7 Part 2, pages 62 to 63

WATER SUPPLIES:

An adequate supply of water should be available at all times and this could be achieved by:

A hydrant supply being installed and ideally within 90 metres of the installation.  The hydrant should be clearly indicated by a plate, affixed nearby in a conspicuous position as detailed in BS 3251:1976

Or

Alternate solutions:

- A charged static tank of at least 45,000litre capacity

- Utilising a spring or river capable of providing / storing at least 45,000 litres of water at all times of the year to which access, space and a hard standing are available for a pumping appliance.

- Any other means of providing a water supply for firefighting operations considered appropriate by the Fire Authority

For further guidance refer to:

- Approved Document B – Fire safety, Volume 2 – Buildings other than dwelling houses, Section 16: Fire mains & Hydrants, B5 pages 164 to 165

- https://www.water.org.uk/guidance/national-guidance-document-on-the-provision-of-water-for-firefighting-3rd-edition-jan-2007/ .

PROPOSED FIRE SAFETY MEASURES WITHIN THE BUILDING

The Fire Authority will have an opportunity to comment on the fire safety measures within the proposed premises during the Building Regulations 2010 Consultation process