## Section
Kingsley Circle
Item No. | Upstream Node | Downstream Node | Dia/Height [mm] | Use | Total Length [m] | Pipe Condition
1 | SJ0451 | SJ0542 | 150 | Surface water | 12.78 | Fractures in line
2 | SJ0542 | MAIN | 150 | Surface water | 22.15 | Debris in line
3 | SJ0510 | SJ0511 | 150 | Foul | 39.1 | Pipe Ok
4 | REAR 13 | SJ0511 | 150 | Foul | 28.77 | Pipe Ok
5 | SJ0511 | SJ0412 | 150 | Foul | 19.27 | Foul deposits in line & possible hole
6 | SJ0513 | SJ0511 | 100 | Foul | 13.35 | Holding water DS
7 | SJ0412 | SJ0450 | 225 | Foul | 19.85 | Debris throughout
8 | SJ0413 | SJ0403 | 225 | Foul | 18.96 | Pipe Ok
9 | SJ0450 | SJ0413 | 225 | Foul | 23.53 | Pipe Ok

## Lateral
Kingsley Circle
Item No. | Upstream Node | Downstream Node | Dia/Height [mm] | Use | Total Length [m] | Surface Type
1 | NOD_00002 | CN_NOD_00002_SJ0451X | 100 | Surface water | 0
0