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Dawn Docx
Prif Swyddog Tân / Chief Fire Officer



	Jenni Perkins
jenni.perkins@wrexham.gov.uk



	
	

	
	Eich Cyf/Your Ref:

Ein Cyf/Our Ref:

Dyddiad/Date:

Gofynner am/Ask for:

Rhif Union/Direct Dial:
	P/2023/0500
80/ 000848- Slgen8a.Temp.1

20/10/2023
Jim Hughes
01286 662999



                                                                                                                  

Dear Madam,

                                   
THE TOWN AND COUNTRY PLANNING ACT 1990 – CONSULTATION
PREMISES: 	Erection of storage & distribution warehouses – H Pack Packaging UK, Davy Way Industrial Estate, Llay
With reference to your consultation dated 6th October 2023 and received on 10th October 2023, attached is our inspection report in respect of application P/2023/0500
If you should require any further information, please do not hesitate to contact the Compliance Officer.

Yn gywir/ Yours faithfully,
[image: \\walesfs.org.uk\Data\Users\jim.hughes\NWFRS RDS Server Farm\Desktop\JimHughes.jpg]
James Francis Hughes GIFireE
 Authorised Fire Safety Inspecting Office
 And on behalf of the North Wales Fire and Rescue Authority







ACCESS FOR FIRE APPLIANCE:
Site access roads should ideally have minimum width of 3.7 metres
Minimum width between gateways of 3.1 metres (If applicable)
Road carrying capacity: Minimum of 12.5 Tonnes
 TURNING FACILITIES:
Fire and Rescue Service appliances should not have to reverse more than 20 metres from the end of an access road.  This could be achieved by having turning circles, a hammerhead facility or other point at which the appliance can turn.
WATER SUPPLIES:
An adequate supply of water should be available at all times and this could be achieved by:
A hydrant supply being installed and ideally within 90 metres of the installation.  The hydrant should be clearly indicated by a plate, affixed nearby in a conspicuous position as detailed in BS 3251:1976
Or
Alternate solutions:
a) A charged static tank of at least 45,000 litre capacity
b)  Utilising a spring or river capable of providing / storing at least 45,000 litres of water at all times of the year to which access, space and a hard standing are available for a pumping appliance.
c) Any other means of providing a water supply for firefighting operations considered appropriate by the Fire Authority


PROPOSED FIRE SAFETY MEASURES WITHIN THE BUILDING

The Fire Authority will have an opportunity to comment on the fire safety measures within the proposed premises during the Building Regulations 2010 Consultation process.





[image: ]Rydym yn croesawu gohebiaeth a galwadau yn y Gymraeg a’r Saesneg - byddwn yn ymateb yn gyfartal i’r ddwy ac yn ateb yn eich dewis iaith heb oedi.

We welcome correspondence and calls in Welsh and English - we will respond equally to both and will reply in your language of choice without delay.
Gwynedd and Anglesey Area Office
North Wales Fire and Rescue Service
Llanberis Road, Caernarfon
Gwynedd LL55 2DF
Tel: 01286 662999
www.northwalesfire.gov.wales
Swyddfa Ardal Gwynedd a Môn
Gwasanaeth Tân ac Achub Gogledd Cymru
Ffordd Llanberis, Caernarfon
Gwynedd  LL55 2DF
Ffôn: 01286 662999   www.tangogleddcymru.llyw.cymru
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