	  [image: image3.png]



	Developer Services
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Tel:   +44 (0)800 917 2652
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Wrexham County Council
16 Lord Street 

WREXHAM

LL11 1LG

	
	Date: 19/11/2018

	
	Our Ref: PLA0038302

	
	Your Ref: P/2018/0898


Dear Sir
Grid Ref: SJ3285650646 332856 350646

Site:   Land off Jacques Way, Wrexham

Development: Erection of affordable housing units comprising 1 detached dwelling, 18 semi-detached dwellings and 6 flats and associated works

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

ASSET PROTECTION

We note from the location plan submitted as part of the application that Jacques Yard Pumping Station has been included within the application site.  We would advise that no notice of application has been served Dwr Cymru Welsh Water as required under Article 10 of The Town and Country Planning (Development Management Procedure) (Wales) Order 2012.

We note from the proposed site plan that some of the dwellings are located in close proximity to Jacques Yard SPS.  We would advise that no dwelling should be located within 15m of Jacques Yard SPS.

The proposed development site is also crossed by a 80mm diameter foul public raising main sewer with its approximate position being marked on the attached Statutory Public Sewer Record. Under Section 159 of the Water Industry Act 1991, Dwr Cymru Welsh Water has rights of access to its apparatus at all times, and as such would require an easement of 3m either side of the centreline of this pipe. Should the proposed development be located within the protection zones of the sewer crossings, there would be a requirement to divert the public sewer, which can be applied for under Section 185 of the Water Industry Act 1991.

SEWERAGE 

Having reviewed the proposal, we note it is proposed for foul flows from the proposed development to be disposed of via the public sewerage system and surface water is to be discharge into a soakaway system. These drainage arrangements are acceptable in principle. However, given the omission of a detailed drainage plan/ layout, we would kindly request that if you are minded to grant Planning Consent for the above development that the following Condition and Advisory Notes are included within the consent to ensure no detriment to existing residents or the environment and to Dwr Cymru Welsh Water's assets.

Condition  

No development shall commence until a drainage scheme for the site has been submitted to and approved in writing by the local planning authority. The scheme shall provide for the disposal of foul, surface and land water, and include an assessment of the potential to dispose of surface and land water by sustainable means. Thereafter the scheme shall be implemented in accordance with the approved details prior to the occupation of the development and no further foul water, surface water and land drainage shall be allowed to connect directly or indirectly with the public sewerage system.

Reason: To prevent hydraulic overloading of the public sewerage system, to protect the health and safety of existing residents and ensure no pollution of or detriment to the environment.

Advisory Notes  

The applicant may need to apply to Dwr Cymru / Welsh Water for any connection to the public sewer under S106 of the Water industry Act 1991. If the connection to the public sewer network is either via a lateral drain (i.e. a drain which extends beyond the connecting property boundary) or via a new sewer (i.e. serves more than one property), it is now a mandatory requirement to first enter into a Section 104 Adoption Agreement (Water Industry Act 1991). The design of the sewers and lateral drains must also conform to the Welsh Ministers Standards for Gravity Foul Sewers and Lateral Drains, and conform with the publication "Sewers for Adoption"- 7th Edition. Further information can be obtained via the Developer Services pages of www.dwrcymru.com 

The applicant is also advised that some public sewers and lateral drains may not be recorded on our maps of public sewers because they were originally privately owned and were transferred into public ownership by nature of the Water Industry (Schemes for Adoption of Private Sewers) Regulations 2011.  The presence of such assets may affect the proposal.  In order to assist us in dealing with the proposal the applicant may contact Dwr Cymru Welsh Water. Under the Water Industry Act 1991 Dwr Cymru Welsh Water has rights of access to its apparatus at all times.

SEWAGE TREATMENT 

No problems are envisaged with the Waste Water Treatment Works for the treatment of domestic discharges from this site.

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
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Alaw Jones

Development Control Officer

Developer Services
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Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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