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	Developer Services

PO Box 3146

Cardiff

CF30 0EH
Tel:   +44 (0)800 917 2652
Fax:   +44 (0)2920 740472

E.mail: developer.services@dwrcymru.com
	Gwasanaethau Datblygu

Blwch Post 3146

Caerdydd

CF30 0EH

Ffôn:  +44 (0)800 917 2652

Ffacs:  +44 (0)2920 740472
E.bost: developer.services@dwrcymru.com



Wrexham County Council
16 Lord Street 

Wrexham
LL11 1LG

	
	Date: 19/04/2018

	
	Our Ref: PLA0033943

	
	Your Ref: P/2018/0289


Dear Sir
Grid Ref: SJ4144739409 341447 339409

Site: Land off Tudor Drive Penley

Development: Discharge of condition 13 - submission of scheme for the construction and integrated drainage of the site

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

SEWERAGE
Having reviewed the Engineering Layout (drawing number J01750/A1/001 Rev E), we note the developer proposes to discharge foul flows into the public foul sewer. It would also appear that surface water runoff from the proposed development is to be discharged into the public surface water sewer.

We object to the proposed discharge of surface water into the public sewer.  From the information submitted, no justification appears to have been provided to support the discharge of surface water into the public sewer.  Due to the sensitivity of allowing surface water to enter the public sewerage system, the developer will have to demonstrate that all other options for surface water drainage have been fully explored and exhausted. Consideration will need to be given to the incorporation of sustainable methods of drainage into the scheme in line with Welsh Government’s ‘Recommended non-statutory standards for sustainable drainage (SuDS) in Wales – designing, constructing, operating and maintaining surface water drainage systems’ (2017).

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
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Alaw Jones

Development Control Officer

Developer Services
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Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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