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	Developer Services

PO Box 3146

Cardiff

CF30 0EH
Tel:   +44 (0)800 917 2652
Fax:   +44 (0)2920 740472

E.mail: developer.services@dwrcymru.com
	Gwasanaethau Datblygu

Blwch Post 3146

Caerdydd

CF30 0EH

Ffôn:  +44 (0)800 917 2652

Ffacs:  +44 (0)2920 740472
E.bost: developer.services@dwrcymru.com



Wrexham County Council
16 Lord Street 

Wrexham
LL11 1LG

	
	Date: 24/03/2020

	
	Our Ref: PLA0048189

	
	Your Ref: SAB/FULL/2020/0202


Dear Sir,
Grid Ref: SJ350504 335035 350499

Site: Land off Eaton Drive, Caia Park, Wrexham

Development: SAB - Proposed development of 16 flats

We refer to your SAB consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

APPRAISAL  

As a statutory consultee, we welcome the opportunity to comment on this SAB application for surface water drainage proposals on land off Eaton Drive, Caia Park, Wrexham, in accordance with Schedule 3 of the Flood & Water Management Act 2010. Our comments are provided in response to the hierarchy (S1) and fixed standards (S2 – S6), as highlighted in the Welsh Government 'Statutory standards for sustainable drainage systems', and on the basis of information provided by the SAB application. Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.  

The submitted application form and accompanying Surface Water & Foul Drainage Scheme General Arrangement Plan ref no. 19134/501 revision A, indicates proposals to use porous paving throughout the development as surface water attenuation storage.  

However, a 150mm diameter foul sewer and 100mm diameter combined sewer crosses the development site, with their approximate positions being marked on the attached plan. In order to perform our Statutory Duty, we have rights of access to our apparatus at all times. Whilst it is acknowledged that it is proposed to divert the public sewers due to the proximity of development, it appears that the proposed porous paving will be constructed above the diverted public sewers.  Under Section 159 of the Water Industry Act 1991, Dwr Cymru Welsh Water has rights of access to its apparatus at all times, and as such no operational development would be allowed within 3m either side of the centreline of these public sewers.

Also, please note that the applicant has not obtained approval under Section 185 of the Water Industry Act 1991 for the diversion of the public sewers. The drainage proposal will be subject to Welsh Minister design and Sewers for Adoption (7th Edition) standards. 

In accordance with Standards S3 and S6, the construction of the proposed drainage system shall take account of health and wellbeing and minimise risks as far as reasonably practicable. We therefore OBJECT and respectfully request this SAB application is refused or otherwise recommend that the proposed SuDS component is repositioned to accommodate for the required protection zone measured 3 metres either side of the centreline of the public sewers. On receipt of this information, we respectfully request that we are re-consulted on this SAB application.

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
Alaw Jones
Development Control Officer

Developer Services

	     [image: image3.png]olas

Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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