MEMORANDUM

From: Ian Jones			To: David Williams

Public Protection Service Manager		Planning Control Manager

Our Ref:		              Your Ref: P/2020/0007

Date: 2nd March 2020

Town and Country Planning Act 1990

Town and Country Planning (General Development Procedure) Order 1996

Re: P/2020/0007 CHAPTER COURT BETWEEN ARGYLE STREET HOPE STREET QUEEN STREET AND RHOSDDU ROAD

Noise Report by RBA Acoustics Ref: 9928.RP01.ENS.0 Prepared: 12 February 2020 Revision Number: 0

The findings of the above noise report are accepted and I recommend that the noise ratings recommended by under both ‘Table 2 – Plant noise Criteria’ and ‘Table 3 – Environmental Noise Criteria’ of the above report be conditioned in any planning permission that be granted:

For the air handling plant:

The rating level of any noise generated by air handling plant associated with the development shall not exceed:

- Daytime (07:00 to 19:00) 40 dBA LAeq at 1m from any Noise Sensitive Premises

- Night Time (23:00 to - 07:00) 35 dBA LAeq at 1m from any Noise Sensitive Premises

The noise levels shall be determined at nearby noise sensitive premises, and measurements and assessment shall be made in accordance with BS4142:2014 Methods for rating and assessing industrial and commercial sound.

For the entertainment noise:

The rating level of any entertainment noise generated by the development shall not exceed:

- Daytime (07:00 to 19:00) 35 dBA LAeq at 1m from any Noise Sensitive Premises

- Daytime (07:00 to 19:00) 35 dBA LAeq at 1m from any Noise Sensitive Premises at 63 Hz

- Night Time (23:00 to - 07:00) 20 dBA  LAeq at 1m from any Noise Sensitive Premises