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	Developer Services

PO Box 3146

Cardiff

CF30 0EH
Tel:   +44 (0)800 917 2652
Fax:   +44 (0)2920 740472

E.mail: developer.services@dwrcymru.com
	Gwasanaethau Datblygu

Blwch Post 3146

Caerdydd

CF30 0EH

Ffôn:  +44 (0)800 917 2652

Ffacs:  +44 (0)2920 740472
E.bost: developer.services@dwrcymru.com



Wrexham County Council
16 Lord Street 

Wrexham
LL11 1LG

	
	Date: 17/02/2018

	
	Our Ref: PLA0032782

	
	Your Ref: P/2018/0110


Dear Sir
Grid Ref: SJ3851750470 338517 350470

Site: Land off Abbey Road Wrexham Industrial Estate

Development: Application for approval of details reserved by conditions imposed under P/2017/1013, Condition 4, 11, 12, 15, 20 and 22

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

SEWERAGE
Having assessed the Drainage Strategy and Flood Risk Assessment produced by MUIR Associates UK (Ltd), we note the developer wishes to discharge both foul and surface water into the combined public sewer located at Abbey Road.  

We object to the proposed discharge of surface water into the public sewer.  From the information submitted, little justification appears to have been provided to support the discharge of surface water into the public sewer.  Due to the sensitivity of allowing surface water to enter the public sewerage system, the developer will have to demonstrate that all other options for surface water drainage have been fully explored and exhausted. Consideration will need to be given to the incorporation of sustainable methods of drainage into the scheme in line with Welsh Government’s ‘Recommended non-statutory standards for sustainable drainage (SuDS) in Wales – designing, constructing, operating and maintaining surface water drainage systems’ (2017).  

It doesn’t appear that a detailed drainage layout plan has been provided as part of the Drainage Strategy and Flood Risk Assessment.  The proposed development site is crossed by a public sewer with the approximate position being marked on the attached Statutory Public Sewer Record. We request that a detailed drainage layout plan be provided to show the proposed point of foul connection with the combined public sewer and demonstrate that a 3 metre easement to either side of the centreline of the public sewer crossing the site is maintained as part of the development.
Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
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   Alaw Jones

   Development Control Officer

   Developer Services
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Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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