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	Developer Services

PO Box 3146

Cardiff

CF30 0EH
Tel:   +44 (0)800 917 2652
Fax:   +44 (0)2920 740472

E.mail: developer.services@dwrcymru.com
	Gwasanaethau Datblygu

Blwch Post 3146

Caerdydd

CF30 0EH

Ffôn:  +44 (0)800 917 2652

Ffacs:  +44 (0)2920 740472
E.bost: developer.services@dwrcymru.com



Wrexham County Council 
16 Lord Street 

Wrexham
LL11 1LG

	
	Date: 27/02/2019

	
	Our Ref: PLA0040838

	
	Your Ref: P/2019/0024


Dear Sir
Grid Ref: SJ3220553120 332205 353120

Site: Gwersyllt County Primary School, Dodds Lane, Gwersyllt, Wrexham

Development: Pursuant to conditions imposed under planning permission P/2018/0745. Condition 3 submission of scheme of surface water drainage

We refer to your planning consultation relating to the above site, and we can provide the following comments in respect to the proposed development. 

We OBJECT to the proposed discharge of surface water into the public sewer.  From the information submitted, little justification appears to have been provided to support the discharge of surface water into the public sewer.  Due to the sensitivity of allowing surface water to enter the public sewerage system, the developer will have to demonstrate that all other options for surface water drainage have been fully explored and exhausted. Consideration will need to be given to the incorporation of sustainable methods of drainage into the scheme in line with Welsh Government’s Statutory standards for sustainable drainage systems – designing, constructing, operating and maintaining surface water drainage systems 2018.  No evidence has been provided that the applicant has explored and exhausted discharging surface water runoff into a surface water body in line with priority level 3 and surface water sewer and highway drainage in line with priority level 4 of the standards.  In addition, no evidence has been received to demonstrate that surface water runoff from the existing site communicates with the public sewerage system.

Our response is based on the information provided by your application.  Should the proposal alter during the course of the application process we kindly request that we are re-consulted and reserve the right to make new representation.

If you have any queries please contact the undersigned on 0800 917 2652 or via email at developer.services@dwrcymru.com
Please quote our reference number in all communications and correspondence.
Yours faithfully, 
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  Alaw Jones

  Development Control Officer

  Developer Services
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Glas Cymru Cyfyngedig




Welsh Water is owned by Glas Cymru – a ‘not-for-profit’ company.

Mae Dŵr Cymru yn eiddo i Glas Cymru – cwmni ‘nid-er-elw’.
	We welcome correspondence in

Welsh and English

Dŵr Cymru Cyf, a limited company registered in

Wales no 2366777. Registered office: Pentwyn Road,

Nelson, Treharris, Mid Glamorgan CF46 6LY
	Rydym yn croesawu gohebiaeth yn y

Gymraeg neu yn Saesneg

Dŵr Cymru Cyf, cwmni cyfyngedig wedi’i gofrestru yng

Nghymru rhif 2366777. Swyddfa gofrestredig: Heol Pentwyn

Nelson, Treharris, Morgannwg Ganol CF46 6LY.
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